00740CTDW

Catwalk Lube Tank

Recommended Guideline Specification

Furnish a 740 gallon UL-142, double-wall rectangular Catwalk Tank, 15’9” long x 3’3” wide x 2’0.5” deep in accordance with Underwriters Laboratories Standard UL-142.

Tanks shall be of all welded construction, fabricated of 10 ga. mild carbon steel. Standard construction shall utilize lap joints with continuous fillet weld on all outside seams. Tank shall include five 2" forged steel fittings and one 4" or 6" forged steel emergency vent fitting for each tank wall. Fabrication shall include 2" high supports welded to the tank underside, providing ground clearance for visual inspection, a 2" high lip around top and steel/FRP grating to cover tank top.

Also provide integral handrail system with two-four shelves and one/two sets of steps.

Standard tank coating is red primer.

Highland tanks are air tested at the factory but MUST be retested at the jobsite by the installer prior to installation.

Tank shall be fabricated by Highland Tank: Stoystown, PA; Manheim, PA; Watervliet, NY; or Greensboro, NC.