**08000OWSAGCYLSWSTDHTC**

Specifier to supply information for all yellow highlighted areas in specification. Contact Highland Tank if additional assistance is required. A [sizing guide](http://www.highlandtank.com/steel-storage-tank-sizing) is available on the Highland Tank web site.

Model HTC Aboveground Cylindrical Single-wall Oil/Water Separator with Corella® Coalescer Plate System

Project Description: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Scope

The separator shall be designed for gravity separation of free oils (hydrocarbons and other petroleum products) along with some settleable solids from wastewater associated with \_\_\_\_\_\_\_\_\_\_\_\_\_\_ operations. Separator shall be prefabricated with inclined, parallel, flat/corrugated plate and impingement coalescers. Separator shall be installed underground with top access at or above grade level. The source of the influent to the separator shall be gravity flow from stormwater runoff, hydrocarbon spills, and/or cleaning/maintenance operations.

Specifications

Provide Highland Tank Model HTC-8000 Aboveground Cylindrical Single-wall Parallel Corrugated Plate Gravity Displacement Oil/Water Separator. Separator shall be furnished with oil level alarm system having a total volume of 8000 gallons to comply with Spill Prevention Control and Countermeasures (SPCC) plan requirements at the facility. The sizing of this oil/water separator is consistent with industry protocols for complying with the minimum federal spill and discharge regulations therefore a separator of smaller volume is not permissible.

Separator to be furnished with a Corella® inclined parallel flat/corrugated plate coalescer to simultaneously separate free oil droplets and settleable or suspended solids particles from water without clogging of the coalescer.

Quantity: \_\_\_\_\_\_

Nominal Dimensions:

Nominal Diameter: 7-feet, 0-inches, as indicated on the drawings.

Nominal Length: 28-feet, 0-inches, as indicated on the drawings

Performance

Influent Characteristics

Provide separator designed for intermittent and variable flows of water, oil, or any combination of non-emulsified oil-water mixtures ranging from zero to 800 gal/min. Nominal separator retention time shall be 10 minutes, based on total unit volume. (Actual retention time will be less due to air space above fluid level).

Typical operating temperature range of the influent oil in water mixture: 40º F to 80º F.

• Installation site operating temperatures: Minimum \_\_\_\_\_ º F, Maximum \_\_\_\_\_ º F.

Typical specific gravity range of the oils at operating temperatures: 0.71 to 0.92.

• Installation site oils specific gravity: \_\_\_\_\_.

Typical specific gravity range of the fresh water at operating temperatures: 1.00 to 1.03.

• Installation site fresh water specific gravity: \_\_\_\_\_.

Effluent Characteristics

The free oil and grease concentration in the effluent from the separator shall not exceed 10 mg/l (10 PPM) to satisfy requirements of the NPDES stormwater discharge permit. To achieve this goal, it will be necessary to remove all free oil droplets equal to and greater than 20 microns.

Design Criteria

Separator shall be designed in accordance with Stokes Law and the American Petroleum Institute Publication 421, "Monographs on Refinery Environmental Control - Management of Water Discharges; Design and Operation of Oil/Water Separators.” The total effective surface area of the parallel-corrugated plate coalescer shall be determined by OWS manufacturer for the flow, temperature, and oil specific gravity conditions specified above. The total effective surface area of the polypropylene impingement coalescer shall be determined by OWS manufacturer for the flow, temperature, and oil specific gravity conditions specified above. Calculations, signed and stamped by a Registered Professional Engineer shall be submitted to document specified effluent quality based on complete removal of the specified oil globule. A separator with lower effective surface areas is not permissible.

Separator capacities, dimensions, construction, and thickness shall be in strict accordance with Underwriters Laboratories, Subject UL-142 Standard for Safety, Steel Underground Tanks for Flammable and Combustible Liquids, Single-wall construction. Separator shall comply with National Fire Protection Association NFPA 30 Flammable and Combustible Liquids Code.

Separator shall be the standard product of a steel tank manufacturer regularly engaged in the production of such equipment. Manufacturer shall have at least 20-years’ experience in manufacturing similar units for identical applications. No subcontracting of tank fabrication shall be permitted.

Separator shall be fabricated, inspected, and tested for leakage before shipment from the factory by manufacturer as a completely assembled vessel (to the greatest extend possible with consideration to shipping requirements) ready for installation.

Separator shall be cylindrical, horizontal, atmospheric-type steel vessel intended for the separation and storage of flammable and combustible liquids. The separator shall have the structural strength to withstand static and dynamic hydraulic loading while empty and during operating conditions. A separator with a reduced shell thickness is not permissible.

Separator shall have the following oil storage capacities:

* High oil level (warning), equal to about 20% of the static vessel volume,
* High-high oil (alarm), equal to about 43% of the static vessel volume,
* Emergency oil spill capacity equal to about 80% of the static vessel volume.

Description

Separator shall be standard prefabricated, inclined parallel-flat / corrugated plate, gravity displacement type unit with removable manway cover(s).

The separator shall be a pre-packaged, pre-engineered, ready to install unit consisting of:

A 10-inch flanged influent connection. An internal influent nozzle at the inlet end of the separator. Nozzle discharge to be located at the furthest diagonal point from the effluent discharge opening.

A non-clogging flow distributor and energy dissipating, velocity head diffusion baffle and stationary under flow baffle at the inlet to:

• reduce horizontal velocity and flow turbulence.

• distribute the flow equally over the separator’s cross-sectional area.

• direct the flow in a serpentine path to enhance hydraulic characteristics and fully utilize all

separator volume.

• completely isolate all inlet turbulence from the separation chamber.

A sediment chamber to disperse flow and collect oily solids and sediments.

A sludge baffle to retain settleable solids and sediment and prevent them from entering the separation chamber.

An Oil/Water Separation Chamber containing a, inclined parallel corrugated plate coalescer with removable corrugated plates sloped downward toward the sediment chamber and sectionalized removable Petro-Screen polypropylene impingement coalescer

Inclined parallel corrugated plate coalescer to:

• shorten the vertical distance than an oil globule must rise for effective removal. Minimum plate gap to be 1-1/4".

• enhance coalescence by generating a slight sinusoidal (wave like) flow pattern thereby causing smaller, slow rising, oil globules to coalesce together on the undersides of the plates forming larger, rapidly rising sheets of oil.

• direct the paths of the separated oil to the surface of the separator.

Sectionalized removable "Petro-Screen" polypropylene impingement coalescer designed to intercept oil globules of less than 20 microns in diameter. Heavy, one-piece impingement coalescers are not permissible.

Two, cylindrical manways complete with removable vapor tight cover, gasket, and bolts.

• one manway shall be placed between the inlet and the parallel flat/corrugated plate coalescer to facilitate access into Sediment Chamber for solids removal

• one manway shall be placed between the parallel flat/corrugated plate coalescer and outlet, over the Petro-Screen Coalescer, to facilitate removable of the sectionalized Petro-Screen Coalescer and to provide access into the Oil/Water Separation Chamber

An internal effluent downcomer at the outlet-end of the separator, to allow for discharge from the bottom of the oil water separator only.

A 10-inch flanged effluent connection.

Two factory supplied saddles, seal welded to the OWS, located as shown on the drawing.

Fittings for vent, interface/level sensor, waste oil pump-out, sampling, and gauge.

Lifting lugs at balancing points for handling and installation.

Identification plates: Plates to be affixed in prominent location and be durable and legible throughout equipment life.

Internal surfaces commercial grit blast and coated with 15 mils DFT heavy-duty polyurethane.

External surfaces commercial grit blast and coated with heavy-duty Epoxy Primer and Urethane Topcoat, Color: White.

Accessories & Options

Separator shall be supplied with an audible and visual alarm system that indicates high oil level (visual only) and high-high oil level (audible and visual) of oil storage in the oil/water separator will be provided. A silence control shall be provided for the audible alarms. Level sensor(s) to be intrinsically safe. Level sensor floats to be made of stainless steel. The control panel shall be NEMA 4. Power to the control panel is to be [ \_\_\_\_\_]-volt, [ \_\_\_\_\_ ]-phase.

Separator shall be supplied with a freeze protection system, consisting of immersion heaters and insulation. Heaters shall be sized to maintain 40ºF inside the insulated OWS, at a minimum ambient temperature of \_\_\_ºF. Insulation shall consist of 2” thickness of closed cell foam, contained without a steel exterior wrap of steel. Insulation to provide a minimum R factor of R14.

Quality Assurance

Submittals:

Shop Drawings: Shop drawings for oil/water separators shall show principal dimensions and location of all fittings.

Instructions: Provide three complete sets of installation, operation, and maintenance instructions with separator.

Quality Control: Quality control and inspection procedures shall be considered part of the submittal package. Quality Control reports shall be available upon request after fabrication.

Warranty

The manufacturer shall warrant its products to be free from defects in material and workmanship for a period of one year from the date of shipment. The warranty shall be limited to repair or replacement of the defective part(s).

Approved Manufacturers

Highland Tank and Mfg. Co., One Highland Road, Box 338, Stoystown, PA 15563,

Phone 814 893-5701, FAX 893-6126, shall manufacture the Oil/Water Separator.

For additional information visit us at [**www.highlandtank.com**](http://www.highlandtank.com/)